## Directions
Directions for using the 62MZCalc spreadsheet |  |  |  |  | Revised November 2016
This spreadsheet is primarily intended to be used to determine the ventilation rate for ventilation systems that serve multiple zones and that recirculate air from one or more zones to other zones. Typical examples are variable air volume (VAV) systems. The spreadsheet may also be used for all other ventilation system types as well - it is not limited to multiple zone systems.
This spreadsheet is easier to use if all zones served by the system are entered -- critical zones are then determined automatically and the spreadsheet automatically determines system level inputs by summing values for the zones. However, both the spreadsheet and the Standard allow the user to enter only those zones that are anticipated to be the critical zones under the operating scenarios to be analyzed. In this case, the user must override system level inputs as described below.
Descriptions of each input variable on the "Vot Calculation" tab are listed below. Variables shown in italics are defined in Standard 62.1-2016. Other variables are used here for convenience and clarity but are not officially defined in the standard.
Editable fields on the "Vot Calculation" are highlighted in yellow.
Note: This spreadsheet relies on Visual Basic macros in order to function properly. Be sure to enable macros. In older versions of Excel, go to Tools --> Macro --> Security. In Excel 2007, go to Office Button --> Excel Options --> Trust Center --> Trust Center Settings --> Macro Settings. Also note that Excel 2007 does not directly support the conversion of macros that were written in earlier versions of Excel. A VBA Converter Pack may be required to use this spreadsheet in Excel 2007. See www.microsoft.com for more information.
Building: |  | Building name or description
System Tag/Name: |  | Ventilation system unit tag, such as AHU-1
Operating Condition Description: |  | Describe the design condition being analyzed. At least the peak cooling and peak heating condition must be evaluated
Units (select from pull-down list) |  | Choose either IP (inch-pound) or SI (Systeme Internationale) from a pull-down list
Inputs for System |  | Name | Units | Description
| Floor area served by system | As | sf or sm | The total floor area served by the system. The total of zones entered below is shown to the right of the last zone and it is entered here as a default. However, not all zones must be analyzed so this total may not be equal to As. The user should override the default value if not all zones are analyzed.
| Population of area served by system | Ps | P | The total number of people served by the system. The total number of people of zones entered below is shown to the right of the last zone and is entered here as a default for system population w/o diversity. However, not all zones must be analyzed so this total may not be equal to Ps. The user should override the default value if not all zones are analyzed. If all zones are entered, occupant diversity may be and usually is taken into account (not all zones will be simultaneously occupied). The system population, Ps, is calculated by multiplying the non-diversified total by the diversity factor, D, which can be entered in cell H/8.
| Design primary supply fan airflow rate | Vpsd | cfm or l/s | The design system primary airflow rate supplied to all zones served by the system from the air handling unit at which the outdoor air intake is located. The total primary airflow of zones entered below is shown to the right of the last zone and is entered here as a default. However, not all zones must be analyzed so this total may not be equal to Vpsd. The user should override the default value if not all zones are analyzed. If all zones are entered, Vpsd may include a zone load diversity, which can be entered in cell H/9. For dual fan dual duct systems with outdoor air only supplied to the cooling fan, Vpsd is the cooling fan design airflow rate; if outdoor air is supplied equally to the heating and cooling fans, enter the sum of the two fan airflow rates.
| OA req'd per unit area for system (Weighted average) | Ras | cfm/sf or l/s/sm | The system building area component rate. If this differs among zones, weight the area component for each zone by the area of each zone. The weighted average of zones entered below is shown in the Check Figure column in this row to the right of the last zone and is the default value entered in this cell. However, not all zones must be analyzed so this average may not be equal to Ras.
| OA req'd per person for system area (Weighted average) | Rps | cfm/p or l/s/p | The system occupant component rate. If this differs among zones, weight the occupant component for each zone by the area of each zone. The weighted average of zones entered below is shown in the Check Figure column in this row to the right of the last zone and is the default value entered in this cell. However, not all zones must be analyzed so this average may not be equal to Rps.
| Percent increase in Vbz over minimum required |  | % | This value increases breathing zone ventilation as a percentage over the minimum required by the standard. For example, to calculate the ventilation needed to meet the requirements of LEED Indoor Environmental Quality (EQ) Credit 2: Increased Ventilation, enter a value of 30% in this field.
| Does system have Outdoor Air Economizer |  |  | Choose either Yes or No from a pull-down list. This switch is used to evaluate if in the heating condition the outdoor air rate provided by the economizer controls would exceed the minimum outdoor air required. If so, a flag will indicate that the analyzed condition is not "critical," meaning it will not fix the minimum outdoor air rate.
Show Values per Zone Button |  |  |  | This button displays each zone input values as well as resulting system values. It provides an optional way to enter and view data and is particularly handy when there are many zones
Inputs for Potentially Critical zones
Not all zones need to be analyzed, only those that are potentially the critical zones. The following provides some guidance in selecting zones for analysis : * Cooling Condition: For single duct systems, the zones most likely to be critical are those with low cooling loads and high occupancy loads. For example, in office buildings, interior conference rooms are almost always the critical zone. Exterior conference rooms with north exposures or shaded glass are also likely candidates. Zones with high envelope cooling loads (e.g. south and west zones) seldom are critical due to their high supply air rates. Zones with low occupant density are also seldom critical zones. * Heating Condition: For single duct systems, the critical zones are generally perimeter zones with low airflow rates, such as north zones. For VAV systems, look for exterior zones that have low minimum primary supply air rates.
The spreadsheet is initially configured for 2 zones. If additional zones are to be evaluated, click the ADD ZONE button. Do not add zones by manually inserting columns since it may result in calculation range errors.
| Zone Name |  |  | Description of ventilation zone. This cell turns purple italic for critical zone(s) (those that are determining the outdoor air rate). Note that a ventilation zone may not be the same as a thermal zone (see Standard for definition).
| Zone Tag |  |  | Ventilation zone tag, typically the terminal unit such as VAV-1. This cell turns purple italic for critical zone(s) (those that are determining the outdoor air rate).
| Space type |  |  | Select an occupancy category from a pull-down list. The Categories are as listed in Table 6-1. Additional rows at the bottom of the table may be used to add new occupancy categories that are established by addenda to the standard.
| Floor Area of zone | Az | sf or sm | Zone net occupiable floor area
| Design population of zone | Pz | P | The design population of the zone. This will default to the number of people calculated using the default occupant density in Table 6-1. It may be overridden to the actual number of people expected to occupy the zone, which in turn may be reduced using time averaging where applicable.
| Design total supply to zone (primary plus local recirculated) | Vdzd | cfm or l/s | The design total rate of air supplied to the space including primary air (air from the AHU that has the outdoor air intake) and air transferred or recirculated from other spaces. Examples of transfer air include: air induced from adjacent spaces with an exhaust fan or induction terminal unit, air supplied by a terminal fan (e.g. fan-powered mixing box), or air supplied by the heating fan of a dual duct system.
| Induction Terminal Unit, Dual Fan Dual Duct or Transfer Fan? |  |  | Select from pull-down list either ITU (induction terminal unit, such as a series or parallel fan-powered mixing box or system-powered induction unit, which can supply air to the zone from a ceiling return air plenum or from another ventilated space), DFDD (dual fan dual duct system, which in addition to the primary ventilation cooling fan includes a parallel heating fan that can supply recirculated air to the zone), or TF (transfer fan, which is a fan that supplies or induces transfer air into the room from another ventilated space). If none of these apply (such as single duct systems or single fan dual duct systems), leave this cell blank (or delete the entry in the cell).
| Frac. of local recirc. air that is representative of system RA | Er |  | The fraction of secondary recirculated air supplied to the zone that is representative of average system return air rather than air directly recirculated from the zone. For systems that fully mix the return air before recirculating it, such as dual fan/dual duct systems, Er is 1.0. For systems with local recirculation fans such as fan-powered boxes or local transfer fans, Er is typically between 0 and 1.0 but can theoretically exceed 1.0. Take for example a fan-powered mixing box. Er will be equal to 1.0 if the fan-powered box intake is located near the main air handler return air opening to the return air plenum, i.e. the return air to the fan-powered box is equal in quality to the return air that is going through the primary air handler. Er would be equal to 0.0 if the fan-powered box inlet were ducted directly to the zone it served, i.e. the quality of the air to the fan-powered box is equal to that in the zone served. In this case, the recirculated air provides no ventilation benefit. Er can be greater than 1 if the recirculated air comes from nearby zones that are over-ventilated relative to the average return air in the system. Most plenum mounted fan-powered box applications will be well between these extremes. A default value of 0.5 is assumed in the spreadsheet, which is usually conservatively low. See results of ASHRAE research project RP-1276 for more details.
Inputs for Operating Condition Analyzed
| Percent of total design airflow rate at conditioned analyzed | Ds | % | The percentage of the design airflow rate at the conditioned being analyzed. For the system, Ds is multiplied by Vpsd to get the ventilation system airflow rate Vps. The cell for the system defaults to the sum of the zone primary airflow rates (shown in the Check Figures columns to the right of the last zone), but since not all zones may be analyzed, this value may not match system Ds. For each zone, Ds is multiplied by Vdzd to get the zone total supply air rate Vdz. For constant volume systems, Ds is 1.0 at both the system and zones. For VAV systems: * Cooling condition. Ds is typically 1.0 for the system. For series fan-powered mixing boxes, Ds is 1.0 for all zones. For other systems in non-critical zones, Ds is either 1 or slightly less to reflect load diversity. For the critical zone(s) Ds will typically be determined based on the zone minimum airflow rate setpoint, although it may be higher to reflect the lowest zone load that can be expected when the space is fully occupied. * Heating condition. Ds will be much lower than 1.0 reflecting the reduction in airflow rate at each zone. If all zones have been entered into the spreadsheet, Ds can be determined explicitly as the sum of the zone primary airflow rates (Ep*Ds*Vddz). If not all zones have been entered, Ds for the system must be estimated. Ds for each zone is determined assuming the zone is in full heating mode.
| Zone air distribution effectiveness at conditioned analyzed | Ez |  | The zone air distribution effectiveness. See Table 6-2, values from which are available from a pull-down menu. This value may vary depending in the condition being analyzed. For instance, for an overhead supply and return system, it may be 0.8 when analyzing the heating condition and 1.0 when analyzing the cooling condition.
| Primary air fraction of supply air at conditioned analyzed | Ep |  | The ratio of Vpz to Vdz. Vpz is the primary airflow supplied to the zone from the air handling unit at which the outdoor air intake is located. It does not include air transferred or air recirculated to the zone by other means. For VAV-system design purposes, Vpz is the lowest zone primary airflow value expected at the condition analyzed. For a single duct system, this value is 1.0. For a fan-powered mixing box system, Vpz is the supply air rate through the VAV damper but does not include the air supplied to the space by the terminal fan that is drawn from the return air plenum. For a dual fan dual duct terminal unit, Vpz is the cold duct air but does not include air supplied by the heating fan.
Inputs for Systems with Outdoor Air Economizers |  |  |  | The following inputs only apply for systems with economizers operating in cold weather (heating design) conditions
| Outdoor air Temperature | Toa |  | The outdoor air temperature at the conditioned being analyzed, typically the heating design temperature.
| Supply Air Temperature | Tp |  | The primary supply air temperature setpoint at the conditioned being analyzed. If the supply air temperature is reset in cold weather, enter the reset temperature.
| Return Air Temperature | Tr |  | The return air temperature at the conditioned being analyzed
| Supply Fan Heat Gain | dTsf |  | Fan heat gain across the supply air fan (=fan BHP*2545/1.08/Vpsd)
| Return Fan Heat Gain | dTrf |  | Fan heat gain across the return air fan (=fan BHP*2545/1.08/Vr)
Results
| System Ventilation Efficiency | Ev |  | The system ventilation efficiency
| Outdoor air intake required for system | Vot | cfm or l/s | The design outdoor air intake rate required for the system
| Outdoor air per unit floor area | Y | cfm/sf or l/s/sm | The outdoor air rate, Vot, divided by the net occupiable floor area, As
| Outdoor air as a % of primary supply air | Y | % | The outdoor air rate, Vot, divided by the design primary supply air rate, Vpsd
The spreadsheet is initially configured with one worksheet for Vot Calculations. To examine different scenarios (e.g. design cooling and design heating), enter all data for one condition then copy this file to a new file. (Copying the worksheet into a new worksheet in the same file is also acceptable but macro buttons will only work in the original worksheet).

## Vot Calculation
Building: | [11 empty] | Note:this is the default
System Tag/Name: | [11 empty] | new column. do not change
Operating Condition Description: | [11 empty] | or delete, or
Units (select from pull-down list) |  | IP | [9 empty] | the "Add zone"
[5 empty] | w/o diversity |  |  |  | w/ diversity |  |  | command will not work
Inputs for System |  | Name | Units |  | System |  | Diversity |  | System |  |  |  | Check Figures |  |  |  | Default totals/averages | 0% | cell used for string conversion
| Floor area served by system | As | sf | [6 empty] | Default entry has been overridden. |  | 0 |  |  |  |  | 0 | 0 | cell used for string conversion
| Population of area served by system | Ps | P |  |  | D | 100% |  | 0 | Default entry has been overridden. |  | 0 | 0 | P/1000 sf |  |  | 0
| Design primary supply fan airflow rate | Vpsd | cfm |  |  |  | 100% |  | 0 | Default entry has been overridden. |  | 0 | 0 | cfm/sf |  |  | 0
| OA req'd per unit area for system (Weighted average) | Ras | cfm/sf |  | 0 |  |  |  |  | Default entry has been overridden. |  | 0 | 0 | ave cfm/sf |  |  | 0
| OA req'd per person for system area (Weighted average) | Rps | cfm/p |  | 0 |  |  |  |  | Default entry has been overridden. |  | 0 | 0 | ave cfm/p |  |  | 0
| Percent increase in Vbz over minimum required |  |  |  | 0%
| Does system have Outdoor Air Economizer |  | Select from pull-down list | [5 empty] | No
Inputs for Potentially Critical zones | [9 empty] | Potentially Critical Zones
| Zone Name | Zone title turns purple italic for critical zone(s) | [7 empty] | enter name | new zone | new zone | Totals/averages
| Zone Tag | [8 empty] | enter tag | New zone ID | New zone ID
| Occupancy Category |  | Select from pull-down list: | [6 empty] | Restaurant dining rooms | Office space | Office space
| Floor Area of zone | Az | sf | [9 empty] | 0 | total sf
| Design population of zone | Pz | P | (default value listed; may be overridden) | [5 empty] | 0 | 0 | 0 | 0 | total P
| Design total supply to zone (primary plus local recirculated) | Vdzd | cfm | [9 empty] | 0 | total cfm
| Induction Terminal Unit, Dual Fan Dual Duct or Transfer Fan? |  | Select from pull-down list or leave blank if N/A:
| Frac. of local recirc. air that is representative of system RA | Er | [7 empty] | 0.5 | 0.5 | 0.5 | 1 | average
Inputs for Operating Condition Analyzed
| Percent of total design airflow rate at conditioned analyzed | Ds | % |  |  |  |  | May need to manually edit Ds: | 100% | 100% | 100% | 100% | 100% | average
| Air distribution type at conditioned analyzed |  | Select from pull-down list: | [6 empty] | CS | CS | CS
| Zone air distribution effectiveness at conditioned analyzed | Ez | [7 empty] | 1 | 1 | 1 | 1 | average | Primary airflow rate to zones
| Primary air fraction of supply air at conditioned analyzed | Ep | [7 empty] | 1 | 1 | 1 | 1 | average | 0 | cfm
Inputs for Systems with Outdoor Air Economizers | [9 empty] | 1 | 1 | 1 | Er for ITU/TF |  | 0% | Percent of design
| Outdoor air Temperature | Toa | Deg F | [5 empty] | 100 | 1 | 1 | 1 | Ep for ITU/DFDD/TF
| Supply Air Temperature | Tp | Deg F | [5 empty] | 57
| Return Air Temperature | Tr | Deg F | [5 empty] | 72
| Supply Fan Heat Gain | dTsf | Deg F | [5 empty] | 2
| Return Fan Heat Gain | dTrf | Deg F | [5 empty] | 0
Results
| System Ventilation Efficiency | Ev | [6 empty] | #DIV/0!
| Outdoor air intake required for system | Vot | cfm | [5 empty] | #DIV/0!
| Outdoor air per unit floor area | Vot/As | cfm/sf | [5 empty] | #DIV/0!
| Outdoor air per person served by system (including diversity) | Vot/Ps | cfm/p | [5 empty] | #DIV/0!
| Outdoor air as a % of design primary supply air | Ypd | % | [5 empty] | #DIV/0! | #DIV/0!
Detailed Calculations
Initial Calculations for the System as a whole
| System primary supply air flow at conditioned analyzed | Vps | cfm | = | Vpsd Ds |  |  | = | 0
| Uncorrected OA intake flow req'd for system | Vou | cfm | = | Rps Ps + Ras As |  |  | = | 0
| Uncorrected OA req'd as a fraction of primary SA | Xs |  | = | Vou / Vps |  |  | = | 0
Initial Calculations for individual zones
| Area outdoor air rate | Ra | cfm/sf | [6 empty] | 0.18 | 0.06 | 0.06
| People outdoor air rate | Rp | cfm/p | [6 empty] | 7.5 | 5 | 5
| Total supply air to zone (at condition being analyzed) | Vdz | cfm |  | Vdzd Ds |  |  |  |  | 0 | 0 | 0 | 0
| Primary airflow to zone (at condition being analyzed) | Vpz | cfm | = | Vdz Ep |  |  | = |  | 0 | 0 | 0 | 0
| Breathing zone outdoor airflow | Vbz | cfm | = | Rp Pz + Ra Az |  |  | = |  | 0 | 0 | 0 | 0
| Zone outdoor airflow | Voz | cfm | = | Vbz / Ez |  |  | = |  | 0 | 0 | 0 | 0
| Fraction of zone supply not directly recirc. from zone | Fa |  | = | Ep + (1-Ep) Er |  |  | = |  | 1 | 1 | 1
| Fraction of zone supply from fully mixed primary air | Fb |  | = | Ep |  |  | = |  | 1 | 1 | 1
| Fraction of zone OA not directly recirc. from zone | Fc |  | = | 1-(1-Ez)(1-Ep)(1-Er) |  |  | = |  | 1 | 1 | 1
| OA fraction required in the supply air to the zone | Zd |  | = | Voz / Vdz |  |  | = |  | 0 | 0 | 0 | 0 | Maximum Zd
| OA fraction required in the primary air to the zone | Zpz |  | = | Voz / Vpz |  |  | = |  | 0 | 0 | 0 | 0 | Maximum Zpz
System Ventilation Efficiency
| Zone Ventilation Efficiency (App A Method) | Evz |  | = | (Fa+FbXs-FcZpzEp)/Fa |  |  | = |  | 1 | 1 | 1
| System Ventilation Efficiency (App A Method) | Ev |  | = | min (Evz) |  |  | = | 1
| System Ventilation Efficiency (Table 6.3 Method) | Ev |  | = | Value from Table 6.3 |  |  | = | 1.15
Minimum outdoor air intake airflow
| Outdoor Air Intake Flow required to System | Vot | cfm | = | Vou / Ev |  |  | = | #DIV/0!
| OA intake req'd as a fraction of primary SA | Y |  | = | Vot / Vps |  |  | = | #DIV/0!
| Outdoor Air Intake Flow required to System (Table 6.3 Method) | Vot | cfm | = | Vou / Ev |  |  | = | 0 | #DIV/0!
| OA intake req'd as a fraction of primary SA (Table 6.3 Method) | Y |  | = | Vot / Vps |  |  | = | #DIV/0! | #DIV/0!
Time-averaging
| Time period with high occupancy | Th | min
| Room height | h | ft | = | [5 empty] | 9
| Time period over which averaging can take place | T | min | = | 3 v / Vbz |  |  | = |  | 0
| Error - sum of all values above will show error | [8 empty] | #DIV/0!
| Error flag | [7 empty] | 1 | TRUE
OA Temp at which Min OA provides all cooling
| OAT below which OA Intake flow is @ minimum |  | Deg F | = | {(Tp-dTsf)-(1-Y)*(Tr+dTrf)}/Y |  |  | = | #DIV/0!
Hidden stuff for data validation
Units
IP |  |  | Yes
SI |  | Induction Terminal Unit | No
Dual Fan Dual Duct
Transfer Fan
Ez Table
1
CS | 1 | Custom Air Change Effectiveness from ASHRAE Standard 129
CSCRH | 0.8 | CS Ceiling supply of cool air
CSCRW | 1 | CSCRH Ceiling supply of warm air 15°F (8°C) or more above space temperature and ceiling return.
CSFR | 1 | CSCRW Ceiling supply of warm air less than 15°F (8°C) above space temperature and ceiling return provided that the 150 fpm (0.8 m/s) supply air jet reaches to within 4.5 ft (1.4 m) of floor level. Note: For lower velocity supply air, Ez = 0.8.
FSCR | 1 | CSFR Ceiling supply of warm air and floor return
FSCR LV | 1.2 | FSCR Floor supply of cool air and ceiling return provided that the 150 fpm (0.8 m/s) supply jet reaches 4.5 ft (1.4 m) or more above the floor. Note: Most underfloor air distribution systems comply with this proviso.
FSCRW | 0.7 | FSCR LV Floor supply of cool air and ceiling return, provided lowvelocity displacement ventilation achieves unidirectional flow and thermal stratification
FSFR | 1 | FSCRW Floor supply of warm air and ceiling return
MUEX | 0.5 | FSFR Floor supply of warm air and floor return
MU--EX | 0.8 | MUEX Makeup supply drawn in near to the exhaust and/or return location
MU--EX Makeup supply drawn in on the opposite side of the room from the exhaust and/or return
Temporary Use:
Zone names that are in use, for the column deletion routine
The names in this list get pasted from the main spreadsheet, and transposed to go horizontal-> vertical
The resulting range gets copied into the delete dialog

## Table 6-1 Rates
Standard 62.1-2016 Outdoor Air Rates (Table 6.2.2.1)
| IP |  | SI |  | Default Occupant Density
Occupancy Category | Rp (cfm/per) | Ra (cfm/ft2) | Rp (L/s-per) | Ra (L/s-m2) | #/1000 ft2 (#/100 m2)
Art classroom | 10 | 0.18 | 5 | 0.9 | 20
Auditorium seating area | 5 | 0.06 | 2.5 | 0.3 | 150
Bank vaults/safe deposit | 5 | 0.06 | 2.5 | 0.3 | 5
Banks or bank lobbies | 7.5 | 0.06 | 3.8 | 0.3 | 15
Barbershop | 7.5 | 0.06 | 3.8 | 0.3 | 25
Barracks sleeping areas | 5 | 0.06 | 2.5 | 0.3 | 20
Bars, cocktail lounges | 7.5 | 0.18 | 3.8 | 0.9 | 100
Beauty and nail salons | 20 | 0.12 | 10 | 0.6 | 25
Bedroom/living room | 5 | 0.06 | 2.5 | 0.3 | 10
Booking/waiting | 7.5 | 0.06 | 3.8 | 0.3 | 50
Bowling alley (seating) | 10 | 0.12 | 5 | 0.6 | 40
Break rooms (General) | 5 | 0.06 | 2.5 | 0.3 | 50
Break rooms (Office) | 5 | 0.12 | 2.5 | 0.6 | 50
Cafeteria/fast-food dining | 7.5 | 0.18 | 3.8 | 0.9 | 100
Cell | 5 | 0.12 | 2.5 | 0.6 | 25
Classrooms (age 9 plus) | 10 | 0.12 | 5 | 0.6 | 35
Classrooms (ages 5–8) | 10 | 0.12 | 5 | 0.6 | 25
Coffee stations | 5 | 0.06 | 2.5 | 0.3 | 20
Coin-operated laundries | 7.5 | 0.12 | 3.8 | 0.6 | 20
Common corridors | 0 | 0.06 | 0 | 0.3
Computer (not printing) | 5 | 0.06 | 2.5 | 0.3 | 4
Computer lab | 10 | 0.12 | 5 | 0.6 | 25
Conference/meeting | 5 | 0.06 | 2.5 | 0.3 | 50
Corridors | 0 | 0.06 | 0 | 0.3 | 0
Courtrooms | 5 | 0.06 | 2.5 | 0.3 | 70
Daycare (through age 4) | 10 | 0.18 | 5 | 0.9 | 25
Daycare sickroom | 10 | 0.18 | 5 | 0.9 | 25
Dayroom | 5 | 0.06 | 2.5 | 0.3 | 30
Disco/dance floors | 20 | 0.06 | 10 | 0.3 | 100
Dwelling unit | 5 | 0.06 | 2.5 | 0.3 | 2
Freezer and refrigerated spaces (<50°F) | 10 | 0 | 5 | 0 | 0
Gambling casinos | 7.5 | 0.18 | 3.8 | 0.9 | 120
Game arcades | 7.5 | 0.18 | 3.8 | 0.9 | 20
General manufacturing (excludes heavy industrial using chemicals) | 10 | 0.18 | 5 | 0.9 | 7
Guard stations | 5 | 0.06 | 2.5 | 0.3 | 15
Gym, sports arena (play area) | 20 | 0.18 | 10 | 0.9 | 7
Health club/aerobics room | 20 | 0.06 | 10 | 0.3 | 40
Health club/weight rooms | 20 | 0.06 | 10 | 0.3 | 10
Kitchen (cooking) | 7.5 | 0.12 | 3.8 | 0.6 | 20
Laundry rooms within dwelling units | 5 | 0.12 | 2.5 | 0.6 | 10
Laundry rooms, central | 5 | 0.12 | 2.5 | 0.6 | 10
Lecture classroom | 7.5 | 0.06 | 3.8 | 0.3 | 65
Lecture hall (fixed seats) | 7.5 | 0.06 | 3.8 | 0.3 | 150
Legislative chambers | 5 | 0.06 | 2.5 | 0.3 | 50
Libraries | 5 | 0.12 | 2.5 | 0.6 | 10
Lobbies | 5 | 0.06 | 2.5 | 0.3 | 150
Lobbies/prefunction | 7.5 | 0.06 | 3.8 | 0.3 | 30
Main entry lobbies | 5 | 0.06 | 2.5 | 0.3 | 10
Mall common areas | 7.5 | 0.06 | 3.8 | 0.3 | 40
Media center | 10 | 0.12 | 5 | 0.6 | 25
Multipurpose assembly | 5 | 0.06 | 2.5 | 0.3 | 120
Multi-use assembly | 7.5 | 0.06 | 3.8 | 0.3 | 100
Museums (children’s) | 7.5 | 0.12 | 3.8 | 0.6 | 40
Museums/galleries | 7.5 | 0.06 | 3.8 | 0.3 | 40
Music/theater/dance | 10 | 0.06 | 5 | 0.3 | 35
Occupiable storage rooms for liquids or gels | 5 | 0.12 | 2.5 | 0.6 | 2
Occupiable storage rooms for dry materials | 5 | 0.06 | 2.5 | 0.3 | 2
Office space | 5 | 0.06 | 2.5 | 0.3 | 5
Pet shops (animal areas) | 7.5 | 0.18 | 3.8 | 0.9 | 10
Pharmacy (prep. area) | 5 | 0.18 | 2.5 | 0.9 | 10
Photo studios | 5 | 0.12 | 2.5 | 0.6 | 10
Places of religious worship | 5 | 0.06 | 2.5 | 0.3 | 120
Reception areas | 5 | 0.06 | 2.5 | 0.3 | 30
Restaurant dining rooms | 7.5 | 0.18 | 3.8 | 0.9 | 70
Sales (except as below) | 7.5 | 0.12 | 3.8 | 0.6 | 15
Science laboratories | 10 | 0.18 | 5 | 0.9 | 25
Shipping/receiving | 10 | 0.12 | 5 | 0.6 | 2
Sorting, packing, light assembly | 7.5 | 0.12 | 3.8 | 0.6 | 7
Spectator areas | 7.5 | 0.06 | 3.8 | 0.3 | 150
Stages, studios | 10 | 0.06 | 5 | 0.3 | 70
Supermarket | 7.5 | 0.06 | 3.8 | 0.3 | 8
Swimming (pool & deck) | 0 | 0.48 | 0 | 2.4 | 0
Telephone closets | 0 | 0 | 0 | 0 | 0
Telephone/data entry | 5 | 0.06 | 2.5 | 0.3 | 60
Transportation waiting | 7.5 | 0.06 | 3.8 | 0.3 | 100
University/college laboratories | 10 | 0.18 | 5 | 0.9 | 25
Warehouses | 10 | 0.06 | 5 | 0.3 | 0
Wood/metal shop | 10 | 0.18 | 5 | 0.9 | 20